| IndusControl Inc. 3170 Ridgeway Drive, VERIFICATION REPORT - ROSEMOUNT Unit #11,Mississauga, ELECTRO-MAGNETIC FLOW MEASUREMENT ON L5L 5R4 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Customer Name: | Region of Niagara |  |  | Site/Plant Address: |  | 1800 St. Paul Avenue |  |  |
| Plant Name: | St. Davids Rechlorination Station |  |  |  |  | Niagara falls. ON |  |  |
| Device Information |  |  |  | Service Information |  |  |  |  |
| Make: | Rosemount |  |  | Date: |  | November 4, 2024 |  |  |
| Model: | 8712 |  |  | Report No: |  | CO1554-2411-09 |  |  |
| Order Code: | NA |  |  | Job No: |  | CO1554-2411 |  |  |
| Serial No.: | 503383 |  |  |  |  |  |  |  |
| Software Version | 5.3.1 |  |  | Flow Details |  |  |  |  |
| Job Location: | West Chamber Flow |  |  | Unit: |  | MLD |  |  |
| Asset ID: | 34341 |  |  | Flow Range: |  | 0-14.725 |  |  |
|  |  |  |  | Current Output: |  | 4-20 mA |  |  |
| Sensor Details |  |  |  | 4 mA Set Point |  | 0 |  |  |
| Line size: | 6" |  |  | 20 mA Set Point |  | 14.725 |  |  |
| Flow Cal Tube No.: | 0904905508908005 |  |  |  |  |  |  |  |
| Mounting: | Remote |  |  |  |  | Inst. Reading | AS FOUND | AS LEFT |
|  |  |  |  |  |  | TOTALIZER (ML) | 385.74 | 385.74 |
|  |  |  |  |  |  | FLOW (MLD) | 0.56 | 0.32 |
| Maintenance Checklist |  |  | Remarks |  |  |  |  |  |
| Visual Inspection: | OK | NOT OK |  |  |  |  |  |  |
| Electrical Inspection: | OK | NOT OK |  |  |  |  |  |  |
| Sensor Installation: | OK | NOT OK |  |  |  |  |  |  |
| Transmitter Installation: | OK | NOT OK |  |  |  |  |  |  |
| Instrument Test Information and Results |  |  |  |  |  |  | SCADA Test Details |  |
| Test-Point as Per Calibration KIT | Calculated Flow (FPS) | Calculated O/P (mA) | UUT Display (FPS) |  | UUT Measured Output (mA) | Deviation (FPS) | Calculated mA | Value on SCADA(MLD) |
| 0.00 | 0.00 | 4.00 | 0.00 |  | 4.00 | 0.00 | 4.00 | 0.00 |
| 3.00 | 3.00 | 5.60 | 2.98 |  | 5.56 | 0.02 | 5.60 | 1.44 |
| 10.00 | 10.00 | 9.33 | 10.03 |  | 9.28 | -0.03 | 9.33 | 4.91 |
| 30.00 | 30.00 | 20.00 | 29.97 |  | 19.98 | 0.03 | 20.00 | 14.69 |
| Information of Tools used for Verification of the Instruments |  |  |  |  |  |  |  |  |
| Details | Tool/Kit 1 |  | Tool/Kit 2 |  |  | Tool/Kit 3 |  |  |
| Device Description: | Calibrator |  | Electrical Multimeter |  |  | N/A |  |  |
| Manufacturer: | Rosemount |  | Fluke |  |  | N/A |  |  |
| Model No: | 8714D |  | 179 |  |  | N/A |  |  |
| * Refer Calibration Tools Certificates submittal for more Information |  |  |  |  |  |  |  |  |
| Verification Test Result: | Passed |  |  | Fail |  | Not Verified |  |  |
| Overall Remarks: | Measurement Works within Specification. Verification test Passed |  |  |  |  |  |  |  |
| Service Technician : | Chetan Parekh |  |  | Stamp/Signature |  |  |  |  |
| Printed Date: | November 4, 2024 |  |  |  |  |  |  |  |
| End of Report Version: 19-12 |  |  |  |  |  |  |  |  |